Standard Operating Procedure

Planned Facilities and Environment-Friendly Measures

«Hospital Name» — Supports FMS.2

Why does this SOP exist? (read this first if you're new) This policy sets out how «Hospital Name» keeps its environment and facilities operating in a planned, environment-friendly manner. It covers: Ensuring facilities and space match the services provided Keeping as-built drawings current Maintaining comprehensible signage Providing potable water and electricity around the clock Providing and regularly testing backup sources for both This policy covers planned facilities and environment-friendly measures specifically. Related duties — like patient assessment, clinical care, medication management, patient rights, infection control, quality and safety monitoring, or hospital governance — are covered in the hospital's other policies, not repeated here. Words marked like this are defaults. A blank marked ________ must be filled before issue. If you're new to this SOP, the short version is: follow the numbered steps below in order — they exist because skipping one of them is exactly how a facility hazard goes unnoticed until it hurts someone.

| SOP No. | [Hospital to define] | Version | 1.0 |
| --- | --- | --- | --- |
| Effective Date | ________ | Review Frequency | Annual, or on change |
| Prepared By | Quality Coordinator Name: ________ Signature: ________ |  |  |
| Approved By | Medical Superintendent Name: ________ Signature: ________ |  |  |

# 1. Purpose

This policy sets out how «Hospital Name» keeps its environment and facilities operating in a planned, environment-friendly manner. It covers: Ensuring facilities and space match the services provided Keeping as-built drawings current Maintaining comprehensible signage Providing potable water and electricity around the clock Providing and regularly testing backup sources for both This policy covers planned facilities and environment-friendly measures specifically. Related duties — like patient assessment, clinical care, medication management, patient rights, infection control, quality and safety monitoring, or hospital governance — are covered in the hospital's other policies, not repeated here. Words marked like this are defaults. A blank marked ________ must be filled before issue.

# 2. Scope

This policy applies to «Hospital Name» staff involved in facilities, utilities, medical gases, and fire or non-fire emergencies, including: Engineering, biomedical, nursing and departmental leaders The Engineering In-Charge The Medical Superintendent Departmental leaders The Quality Coordinator This policy covers planned facilities and environment-friendly measures specifically. Related duties are covered in the hospital's other policies, not repeated here, including: Patient assessment Clinical care Medication management Patient rights Infection control Quality and safety monitoring Hospital governance

# 3. Responsibility

Facility Manager / Engineering In-Charge: owns the equipment, inventories, inspection schedules and maintenance plans this policy requires, and keeps the required records current.

Medical Superintendent: escalation point for any gap not being closed, and signs off risk assessments before major facility work.

Quality Coordinator: audits this policy periodically, checks records against the steps below, and flags gaps for corrective action.

Department Heads / Nursing In-charges: report facility hazards or equipment issues in their own area promptly and support inspection rounds.

# 4. Plain-Language Glossary

If a word below is unfamiliar, this is what it means in this SOP:

NFPA: The National Fire Protection Association — a US-based body whose fire and life-safety codes (like NFPA 101 and NFPA 99) are widely used worldwide, including as a reference standard in Indian hospital fire-safety planning.

National Building Code (NBC): India's national reference code (published by the Bureau of Indian Standards) covering building design, including fire and life safety.

IS 10500: India's national drinking-water quality standard, specifying the biochemical and microbiological limits water must meet.

# 5. Procedure

## 5.1 Facilities and space provisions are appropriate to the scope of services

Why this step matters: A department squeezed into space that doesn't match what it actually does is a safety and quality problem hiding behind a floor plan — this record proves space was actually checked against real service scope. NABH checks this as part of how a genuinely safe physical environment actually runs, not just what's written about it.

1. Map the space actually available for each department against the services that department is expected to provide, and flag any mismatch.

2. Where a national or international guidance document sets a specific space or layout requirement for a service (for example AERB guidance for a radiation area), use that document's actual figures rather than an internal estimate.

3. Escalate any service found listed with no matching space, rather than letting the mismatch stand unaddressed. (Records 1–3)

## 5.2 As built and updated drawings are maintained as per statutory requirements.

Why this step matters: Fighting a fire or a burst pipe with an out-of-date drawing costs the minutes that matter most — this record proves the drawings on file actually match the building as it stands today. NABH checks this as part of how a genuinely safe physical environment actually runs, not just what's written about it.

1. Maintain one current as-built drawing set — site layout, floor plans, floor-wise evacuation plans, and the separate civil, electrical, ELV, plumbing, HVAC, medical-gas and IT drawings — matching the statutory building-approval requirement for this site.

2. Name a single custodian responsible for keeping the drawing set current.

3. Update the drawings whenever a real facility change happens, and log the date of that update against the specific change — a drawing set nobody has touched in years after several renovations is not 'as-built' any more. (Records 4–6)

## 5.3 There are internal and external sign postings in the organisation in a manner understood by the patient, families and community.

Why this step matters: Signage nobody can actually read or understand doesn't help a frightened family find the OT in an emergency — this record proves the signs are real, checked and in a form people actually understand. This is a CORE requirement — NABH treats it as non-negotiable, not aspirational.

1. Walk the facility and inventory every sign by area, noting the language(s) used, whether it also uses pictorial/tactile elements, and whether it needs bilingual coverage for this hospital's actual patient population — following the inclusive-signage principles in the Harmonized Guidelines for Standards of Accessibility.

2. Check signage against whatever statutory posting requirement applies to this specific site (fire-exit signage, radiation-area signage, etc.).

3. Repeat the signage walk at least quarterly and keep that record — signage gets removed, damaged or blocked more often than people expect. (Records 7–9)

Technical source(s) for these steps:

Office of the Chief Commissioner for Persons with Disabilities, Government of India — Harmonized Guidelines and Space Standards for Barrier-Free Built Environment.

## 5.4 Potable water and electricity are available round the clock

Why this step matters: Water or power that quietly falls short of standard is invisible until a patient is harmed by it — this record proves it was actually tested, not just assumed safe. This is a CORE requirement — NABH treats it as non-negotiable, not aspirational.

1. Test the hospital's potable water against IS 10500 — biochemical parameters at least quarterly, microbiological parameters at least monthly — and keep the results, not just a 'water is fine' assumption.

2. Where dialysis is in scope, additionally test the reverse-osmosis inlet water for endotoxin, since dialysis water has a stricter safety requirement than general potable water.

3. Log every unplanned water or power outage in a care area and confirm the emergency continuity plan actually activated — a continuity plan that exists but never actually switches on when needed is not meeting this. (Records 10–12)

Technical source(s) for these steps:

Bureau of Indian Standards (2012). IS 10500:2012 — Drinking Water — Specification (Second Revision).

## 5.5 Alternate sources for electricity and water are provided as a backup for any failure / shortage.

Why this step matters: A backup source that exists on paper but was never sized against real demand fails exactly when the primary source does — this record proves the backup can genuinely carry the load. NABH checks this as part of how a genuinely safe physical environment actually runs, not just what's written about it.

1. Name every backup source the hospital actually has — diesel generator, solar, UPS, bore-well/tanker/extra storage tanks — in one inventory, matched to the emergency and standby power planning approach in NFPA 110.

2. Calculate the electrical load each backup source needs to cover and check it against actual critical-area demand — a generator too small for the real load is not a working backup.

3. Name, for each critical area, exactly which backup path covers it, so nobody has to work that out during an actual failure. (Records 13–15)

Technical source(s) for these steps:

National Fire Protection Association — NFPA 110, Standard for Emergency and Standby Power Systems.

## 5.6 The organisation tests the functioning of these alternate sources at a predefined frequency.

Why this step matters: A backup generator nobody has actually started in months is a backup in name only — this record proves it was tested for real, on schedule. NABH checks this as part of how a genuinely safe physical environment actually runs, not just what's written about it.

1. Test every backup source at a fixed, predefined frequency (default monthly for a diesel generator, following NFPA 110's testing discipline for standby power systems) — an untested backup is a backup you're only hoping works.

2. Where an emergency water source was actually used on any occasion, keep a water-acceptance test record for that occasion specifically.

3. Where a test fails, open a corrective-action record and re-test after the fix — don't just note the failure and move on. (Records 16–18)

Technical source(s) for these steps:

National Fire Protection Association — NFPA 110, Standard for Emergency and Standby Power Systems.

# 6. Records

This SOP produces and maintains Records 1 through 18 (see the FMS.2 Records folder).

# 7. Related Documents

Policy on Planned Facilities and Environment-Friendly Measures (HCO/FMS/POL/02) — this policy

Required Records — FMS.2 (see FMS.2 Records folder)

# 8. Where This SOP's Requirements Come From (Verified Sources)

National Accreditation Board for Hospitals and Healthcare Providers. (2025). NABH accreditation standards for hospitals (6th ed.), FMS.2. ISBN 978-81-965264-9-8. https://portal.nabh.co/images/Standards/NABH%20Hospital%20Accreditation%20Standard%206th%20Edition%20January%202025.pdf

# 9. Review

This SOP is reviewed at least annually by the Quality Coordinator together with the Facility Manager, and immediately if an incident, audit or drill finds it isn't working as written.