FMS.6.d — Alternate sources for medical gases, vacuum and compressed air are provided for, in case of failure.

FMS.6 Record 11 — Alternate sources for medical gases, vacuum and compressed air are provided for, in case of failure.

What is this record, in plain terms? This record is where you keep the proof for: “Automatic-changeover test record.” — the specific evidence element Alternate sources for medical gases, vacuum and compressed air are provided for, in case of failure. of this policy asks for. Every time this happens for real, whoever is responsible adds one new row below with: Test Date, Item/System Tested, Result, Tested By, Next Test Due. A worked example row is already filled in below (shaded) so you can see exactly what a completed real entry looks like — replace it, or add your own rows below it, but don't leave the example mixed in with real data.

A real example of when you'd use this The Facility Engineer uses this record whenever a standby gas/vacuum source is inventoried, changeover-tested, or its readiness confirmed. The worked example below shows a real entry: on 20-Jan-2026, item/system tested was “Automatic changeover, oxygen manifold”, tested by was “Biomedical Engineer”, next test due was “20-Feb-2026” — so result was “Switched to standby bank within 1 second on simulated primary-source failure”.

Why does NABH ask for this? A standby gas or vacuum source that's never actually tested for readiness is a backup in name only — this record proves it genuinely works on demand. This is a CORE requirement — NABH treats it as non-negotiable, not aspirational.

How to fill this in — column by column

Test Date: The actual date this test was carried out — not the scheduled date if it slipped.

Item/System Tested: The specific item or system tested — name it precisely.

Result: What actually happened during the test — a real result, not 'passed' with no detail.

Tested By: Who actually carried out the test.

Next Test Due: When this is next due to be tested.

The first data row below (shaded yellow, and marked WORKED EXAMPLE in the row itself) is a worked example already filled in correctly. Delete it or overwrite it once you start using this record for real — don't leave the example row mixed in with real entries. Add more blank rows as needed; don't create a second copy of this file.

| Test Date | Item/System Tested | Result | Tested By | Next Test Due |
| --- | --- | --- | --- | --- |
| WORKED EXAMPLE — TRAINING ONLY — NOT AN ACTUAL HOSPITAL RECORD |  |  |  |  |
| 20-Jan-2026 | Automatic changeover, oxygen manifold | Switched to standby bank within 1 second on simulated primary-source failure | Biomedical Engineer | 20-Feb-2026 |