FMS.1.e — Alternate sources for electricity and water are provided as a backup for any failure/shortage and their functioning is tested at a predefined frequency.

FMS.1 Record 5 — Alternate source loaded backup-test record

What is this record, in plain terms? A record of loaded backup tests -- generator/UPS carrying the essential circuit load, and alternate water actually moving tank-to-tap -- not a no-load crank or a sealed tanker contract nobody has called.

A real example of when you'd use this The monthly generator test is run with the OT, ICU and emergency lighting circuits on load for 30 minutes, not just started and left idling; the result, fuel level and any fault are logged.

Why does NABH ask for this? NABH requires alternate electricity and water sources to be tested at a predefined frequency -- a Commitment requirement that a start-only test does not satisfy.

How to fill this in — column by column

Date of Test: Date the loaded test was run.

Source Tested: Generator / UPS / reserve tank / second borewell / tanker.

Test Type: Loaded (essential-circuit load) or tank-to-tap water movement.

Result (Pass/Fail): Whether the source carried the load or moved water as required.

Fault/Observation: Any fault found, e.g. changeover delay, low battery, seized valve.

Confirmed By: Named engineering lead present at the test.

The first data row below (shaded yellow, and marked WORKED EXAMPLE in the row itself) is a worked example already filled in correctly. Delete it or overwrite it once you start using this record for real — don't leave the example row mixed in with real entries. Add more blank rows as needed; don't create a second copy of this file.

Where this requirement comes from (verified, clickable sources)

• Bureau of Indian Standards. (2016). National Building Code of India, 2016.

| Date of Test | Source Tested | Test Type | Result (Pass/Fail) | Fault/Observation | Confirmed By |
| --- | --- | --- | --- | --- | --- |
| 12/04/2026 | Diesel generator | Loaded (OT+ICU+emergency lighting, 30 min) | Pass | None | Engineering Lead «Name» |