Standard Operating Procedure

Planned Facilities, Utilities and Environment-Friendly Measures

«Hospital Name» — SOP-FMS.1 — Version 1.0

| SOP No. | SOP-FMS.1 | Version | 1.0 |
| --- | --- | --- | --- |
| Effective Date | «________» | Review Frequency | Annual, or on change |

# 1. Purpose

This SOP tells facilities, engineering, clinical and quality staff, in one place, how this hospital keeps its built space matched to what it actually treats; keeps potable water and electricity live around the clock, including at night; proves its backup sources actually carry load rather than just crank once a week; and records real energy and environment initiatives instead of a green-hospital poster. If you hold drawings, watch utilities, run a backup test, or own the energy file, this SOP is for you.

A night-shift engineer finds the OT scrub sink dry at 2am. This SOP is what tells them which record to check, what counts as a failure (a dry point of use, whatever the roof tank shows on paper), and which alternate source should have carried it -- and that the alternate source's last loaded test, not just its last no-load crank, is what proves it should have worked.

We do this because a building that looks fine on a drawing can still fail a patient at 2am. Matching space to what we actually treat, keeping water and power live through the night, and proving backups really carry load under pressure -- these are what stand between a patient and a building that quietly stopped working for them.

To define how «Hospital Name» keeps its physical facilities, drawings, wayfinding, potable water, electricity and their backups matched to the services it actually runs, available round the clock, and genuinely tested -- and how it records real initiatives toward an energy-efficient and environment-friendly hospital, rather than a certificate on a wall.

# 2. Scope

so everyone knows which building failure belongs here and which belongs to a different SOP -- that's what gets the right person responding fast, instead of a dry tap or a dark corridor being nobody's problem for an hour.

Applies to every area of «Hospital Name» that depends on built space, potable water or electricity: clinical, diagnostic, utility, storage and staff areas alike. Does not cover medical and support-service equipment, medical gases, fire and non-fire emergency response, radiation signage, or biomedical-waste handling -- those remain their own SOPs. See Related SOPs.

# 3. Responsibility

a dark essential circuit or a dry clinical tap left unowned stays broken. Naming exactly who holds drawings, who watches utilities and who owns the backup tests is what gets it fixed before a patient is affected, not after.

Head of the Institution: Is accountable that facilities actually operate as this SOP requires.

Named Facilities/Engineering Lead: Holds drawings, utility availability and quality-test records, loaded backup-test records, and the energy-initiative file.

Clinical Heads: Confirm that built space still matches the services their department actually runs.

Quality/Accreditation Coordinator: Audits a sample of the records this SOP produces, at «Hospital to define» frequency, and flags a mismatch rather than filing it.

All Staff: Treat a dark essential circuit, a dry clinical tap, a drawing that doesn't match the floor, or a green poster with no initiative behind it, as defects to report.

# 4. What to do

## Keeping built space matched to what we actually treat

A corridor pressed into service as a ward, or a sluice used as a sterile store, puts patients in a space that was never built to keep them safe. Matching the building to what we actually treat is what prevents that.

Our service directory is the single source of what this hospital actually provides; this step is the built match to it -- waiting, clinical, diagnostic, utility, storage and staff space that can physically hold those services.

«Hospital to define: how facilities and space are shown to be appropriate to the services actually offered.»

A service not in the directory is a recorded absence here, not a gap to be explained away.

## Keeping building drawings current

If a fire crew or a contractor is working from a drawing that doesn't match what was actually built, they can open the wrong panel or miss a wall that's no longer there. Current drawings are what keep that from happening.

We keep one controlled, as-built set covering architectural, structural, electrical, plumbing, fire/detection and medical-gas drawings.

«Hospital to define: how as-built drawings are kept current and who holds the controlled set.»

The set is updated whenever the building or a major service run changes -- an update log, not a one-time filing.

## Signs people can actually read and follow

A first-time family that can't find the entrance, registration, toilets or an exit -- in a language they actually read -- is lost in a building when they're already stressed. A sign nobody can read is a sign that was never posted.

«Hospital to define: internal and external signage in the languages and scripts our actual patients need.»

Signage is checked for faded, missing or contradictory signs on a set schedule.

## Water and power that stay on, day and night

A roof tank that looks full on paper while the OT scrub sink is dry because a valve is shut, or a theatre going dark because a changeover never closed, is a patient-safety failure that happens at the exact moment someone needs water or power most -- often at 3am, not during the morning check.

Points of use for drinking, clinical wash, kitchen, CSSD and dialysis (where we offer it) must actually deliver water on demand, day and night.

«Hospital to define: potable-water quality-testing parameters, sample points and interval.» Where dialysis isn't offered, that's a recorded absence, not a gap.

Essential clinical and life-safety circuits -- at minimum emergency, OT, labour, ICU/HDU, nursery and blood bank where present, ventilators and their compressors, emergency lighting, fire detection, and medical-gas plant alarms -- stay energised at all times.

«Hospital to define: how round-the-clock availability is watched, recorded and restored,» covering night and holiday coverage, not only daytime checks.

## Backup power and water that are actually tested

A weekly no-load crank proves the starter motor works, not that the generator will carry theatre, ICU and emergency lighting together when it's actually needed. A sealed tanker contract nobody has called at night is not a backup -- it's a promise.

Alternate electricity is the source that carries our essential circuits when incoming supply fails: diesel generator, UPS/inverter for circuits that can't tolerate a start delay, and any automatic mains-failure changeover.

«Hospital to define: the alternate-electricity source, essential-circuit list, loaded-test method and test frequency» -- a loaded test under the essential-circuit load, not the workshop socket.

Alternate water is the source that actually moves water to points of use when the main supply fails: reserve tanks with working float valves, a second borewell if available, a tanker contract that can deliver at night, pumps that auto-start.

«Hospital to define: the alternate-water source, the test that proves water actually moves, and the test frequency» -- a tank-to-tap movement record, not a sealed contract.

## Real energy and environment initiatives

A filed electricity bill or a single LED retrofit offered as the whole programme doesn't actually reduce what this hospital consumes or throws away. A real initiative with a measured result is what makes this more than a poster on a wall.

«Hospital to define: the energy-efficient and environment-friendly initiatives this hospital actually runs this year,» each with a named owner, a baseline, and a recorded result -- not a poster.

Eligible initiatives include measured electricity or fuel use, lighting or HVAC set-back in non-clinical hours, solar if installed, rainwater or condensate reuse if installed, segregation of municipal (non-biomedical) waste, and reduction of single-use non-clinical materials.

Shutting HVAC in clinical areas in the name of efficiency is not this -- that's the water-and-power item above failing instead.

# 5. Records

This SOP produces and maintains Records 1-6 (see the FMS.1 Records folder).

# 6. Related SOPs

Hospital's Service Directory (AAC.1)

Radiation/PC-PNDT Signage Policy (AAC.6.e)

Medical and Support-Service Equipment Programme (FMS.3)

Medical Gases, Vacuum and Compressed Air SOP (FMS.4)

Fire and Non-Fire Emergencies SOP (FMS.5)

Support-Services Infection-Control Policy (HIC.3)

# 7. Review

This SOP is reviewed annually, or sooner if a loaded backup test fails, if the service directory changes, or if a related SOP listed above is updated.

# Appendix — NABH Standard Cross-Reference and Evidence Basis

For the Quality Coordinator and NABH assessment use only. The reasoning and real-world triggers for each requirement are already in the body above -- this appendix adds only what the body deliberately leaves out: the exact objective-element code, how this SOP's scope is kept separate from neighbouring standards, and the verified technical source for anything cited.

## Keeping built space matched to what we actually treat — FMS.1.a

Boundary with other standards:

• The AAC.1 service directory is the single source of truth this step is matched against.

Verified source(s):

• National Health Mission. (2022). Indian Public Health Standards.

• Bureau of Indian Standards. (2016). National Building Code of India, 2016.

## Keeping building drawings current — FMS.1.b

Boundary with other standards:

• Named facilities lead holds the controlled set; FMS.4 and FMS.5 are users of specific sheets, not second masters of this record.

Verified source(s):

• Bureau of Indian Standards. (2016). National Building Code of India, 2016.

## Signs people can actually read and follow — FMS.1.c

Boundary with other standards:

• Radiation/PC-PNDT signage and emergency exit displays are separate documents; this step must be consistent with both but doesn't duplicate or replace either.

## Water and power that stay on, day and night — FMS.1.d (Core)

Boundary with other standards:

• Kitchen water is owned by HIC.3 and used here only as a utility point; dialysis water follows the haemodialysis-water framework.

• Fire detection (FMS.5) and medical-gas plant/manifold alarms (FMS.4) are named here as essential circuits, not restated as this step's own programme.

Verified source(s):

• World Health Organization. (2011). Guidelines for Drinking-water Quality (4th ed.).

• Coulliette, A. D., & Arduino, M. J. (2013). Hemodialysis and water quality. Seminars in Dialysis, 26(4), 427-438.

## Backup power and water that are actually tested — FMS.1.e

Boundary with other standards:

• A utility failure that becomes a declared emergency is handed to FMS.5; this step is the test that happens before that night, not the emergency response itself.

Verified source(s):

• Bureau of Indian Standards. (2016). National Building Code of India, 2016 (as the framework pointing to IS 732 wiring practice and IS 3043 earthing).

## Real energy and environment initiatives — FMS.1.f (Excellence, ASTERISKED)

Boundary with other standards:

• Biomedical-waste colour coding, transport and SPCB compliance remain HIC.3's; this step doesn't restate or duplicate that SOP.

Verified source(s):

• Dhillon, V. S., & Kaur, D. (2015). Green hospital and climate change: Their interrelationship and the way forward. Journal of Clinical and Diagnostic Research.

## Full reference list

• National Accreditation Board for Hospitals and Healthcare Providers. (2022). Standards for Small Healthcare Organisations (3rd ed.). NABH SHCO Accreditation Programme page. Facility Management and Safety chapter, standard FMS.1.

• Bureau of Indian Standards. (2016). National Building Code of India, 2016. Occupancy, means-of-egress and services-drawing framework as applied by the local building and fire authority; not a universal mandate.

• World Health Organization. (2011). Guidelines for Drinking-water Quality (4th ed.). Potable-water quality-testing framework, not a pasted protocol or a NABH interval.

• Coulliette, A. D., & Arduino, M. J. (2013). Hemodialysis and water quality. Seminars in Dialysis, 26(4), 427-438. Dialysis-water framework, used only where dialysis is a service this hospital provides.

• Dhillon, V. S., & Kaur, D. (2015). Green hospital and climate change: Their interrelationship and the way forward. Journal of Clinical and Diagnostic Research. Energy-efficiency framework, not a named green-building rating mandate.

• National Health Mission. (2022). Indian Public Health Standards. Space-planning framework, not a NABH bed-count mandate.